## 6DN(E)
6DN Engine Technical data
Engine model | CA6DN1J-45D | CA6DN1-45D
Type | 6-cylinder 4-stroke
Air intake type | Turbocharged&intercooling
Cooling mode | Water cooling
Governor mode | Electron | ECU
Bore×Stroke(mm） | 131×155
Compression ratio | 18∶1
Rated speed(rpm) | 1500
Displacement(L) | 12.53
Rated power(without fan)(kW) | 332
Standby power(without fan)(kW) | 365
Fuel consumption(g/kWh) | 195 | 191
Oil consumption(L/h) | 0.06
Steady state speed regulation(%) | ≤3 | ≤1
Oil capacity including filter(L) | 42
Emission compliant | StageⅡ | EuroⅢ
The flywheel shell interface | SAE1
Flywheel for 14″flexible coupling
Dry weight of base(kg) | 1230
Dry weight of Gen Pac(kg) | 1495
Overall dimension（G.P）(mm) | 2300×1120×1580
Fan consumption（kW） | 11
27℃ air consumption（m3/min） | 22.7
Heat rejection of exhaust（kW） | 240
Exhaust gas temperature after turbine（℃） | 470
Exhaust gas flow（m3/min） | 64.5
Heat rejection from engine（kW） | 20
Heat rejection of coolant（kW） | 149
Base configuration | Standard configuration(add on the base)
Engine with fan | Intake and exhaust sysytem：Air filter and connecting pipes;Connecting flang of exhaust pipe
Alternator 75A 28V | Cooling system: Radiator ;Connecting pipes;Fan guard;Belt guard
Starter motor 7.5KW 24V | Extendable base frame;Manual oil drain pump
Note on A12: 作者: 不带风扇

## 6DM (E)
6DM Engine Technical date
Engine model | CA6DM2-39D | CA6DM2-41D | CA6DM2J-39D | CA6DM2J-41D
Type | 6-cylinder 4-strock
Air intake type | Turbocharged&intercooling
Cooling mode | Water cooling
Governor mode | ECU |  | Electron
Bore×Stroke(mm） | 123×155
Compression ratio | 17.5∶1
Rated speed(rpm) | 1500
Displacement(L) | 11.05
Rated power(without fan)(kW) | 287 | 300 | 287 | 300
Standby power(without fan)(kW) | 316 | 330 | 316 | 330
Fuel consumption(g/kWh) | 189 |  | 195
Oil consumption(L/h) | 0.06
Steady state speed regulation(%) | ≤1 |  | ≤3
Oil capacity including filter(L) | 38
Emission compliant | EuroⅢ |  | StageⅡ
The flywheel shell interface | SAE1
Flywheel for 14″flexible coupling
Dry weight of base(kg) | 1050
Dry weight of Gen Pac(kg) | 1435
Overall dimension(base)(mm) | 1365×773×1192
Overall dimension(G.P)(mm) | 2300×1120×1580
Fan consumption（kW） | 11
27℃ air consumption（m3/min） | 20 | 21 | 20 | 21
Heat rejection of exhaust（kW） | 200 | 215 | 200 | 215
Exhaust gas temperature after turbine（℃） | 460 | 470 | 460 | 470
Exhaust gas flow（m3/min） | 56 | 60 | 56 | 60
Heat rejection from engine（kW） | 16.8 | 18 | 16.8 | 18
Heat rejection of coolant（kW） | 126 | 135 | 126 | 135
Base configuration | Standard configuration(add on the base)
Engine with fan | Intake and exhaust sysytem：Air filter and connecting pipes;Connecting flang of exhaust pipe
Alternator 75A 28V | Cooling system: Radiator ;Connecting pipes;Fan guard;Belt guard
Starter motor 7.5kW 24V | Extendable base frame;Manual oil drain pump
Note on A12: 作者: 不带风扇

## 6DL(E)
6DL Engine Technical date
Engine model | CA6DL1-24D | CA6DL2-27D | CA6DL2-30
Type | 6-cylinder 4-stroke
Air intake type | Turbocharged&intercooling
Cooling mode | Water cooling
Governor mode | Electron
Bore×Stroke(mm） | 110×135 | 112×145
Compression ratio | 17.5∶1
Rated speed(rpm) | 1500
Displacement(L) | 7.7 | 8.57
Rated power(without fan)(kW) | 176 | 205 | 227
Standby power(without fan)(kW) | 194 | 226 | 251
Fuel consumption(g/kWh) | 196 | 195 | 195
Oil consumption(L/h) | 0.06 | 0.0594 | 0.06
Steady state speed regulation(%) | ≤3
Oil capacity including filter(L) | 28 | 30 | 30
Emission compliant | StageⅡ
The flywheel shell interface | SAE2
Flywheel for 11.5″flexible coupling
Dry weight of base(kg) | 780 | 800 | 800
Dry weight of Gen Pac(kg) | 1110 | 1131 | 1131
Overall dimension(base)(mm) | 1345×750×1150
Overall dimension(G.P)(mm) | 1698×948×1490
Fan consumption（kW） | 8 | 9 | 9
27℃ air consumption（m3/min） | 12 | 14 | 15
Heat rejection of exhaust（kW） | 126 | 140 | 160
Exhaust gas temperature after turbine（℃） | 460 | 460 | 470
Exhaust gas flow（m3/min） | 34 | 40 | 45
Heat rejection from engine（kW） | 10.8 | 12 | 13.2
Heat rejection of coolant（kW） | 86 | 96 | 106
Base configuration | Standard configuration
Engine with fan | Intake and exhaust sysytem：Air filter and connecting pipes;Connecting flang of exhaust pipe
Alternator 75A 28V | Cooling system:Radiator ;Connecting pipes;Fan guard;Belt guard
Starter motor 6kW 24V | Extendable base frame;Manual oil drain pump
Note on A12: 作者: 不带风扇

## 6DF(E)
6DF Engine Technical Date
Engine model | CA6DF2D-14D | CA6DF2-17D | CA6DF2-19D
Type | 6-cylinder 4-stroke
Air intake type | Turbocharged |  | Turbo&intercool
Cooling mode | Water cooling
Governor mode | Electron
Bore×Stroke(mm） | 110×115 |  | 110×125
Compression ratio | 17∶1
Rated speed(rpm) | 1500
Displacement(L) | 6.56 |  | 7.12
Rated power(without fan)(kW) | 96 | 125 | 140
Standby power(without fan)(kW) | 105 | 138 | 154
Fuel consumption(g/kWh) | 202 | 202 | 200
Oil consumption(L/h) | 0.08 | 0.08 | 0.06
Steady state speed regulation(%) | ≤3
Oil capacity including filter(L) | 20 |  | 23
Emission compliant | StageⅡ
The flywheel shell interface | SAE3 | SAE2
Flywheel for 11.5″flexible coupling
Dry weight of Gen Pac(kg) | 850 | 880 | 1000
Overall dimension（st）(mm) |  | 1386×680×1100
Fan consumption（kW） | 8
27℃ air consumption（m3/min） | 7 | 9 | 12
Heat rejection of exhaust（kW） | 77 | 102 | 120
Exhaust gas temperature after turbine（℃） | 460 | 470 | 470
Exhaust gas flow（m3/min） | 19 | 25 | 30
Heat rejection from engine（kW） | 14 | 18 | 21
Heat rejection of coolant（kW） | 60 | 77 | 81
Base configuration | Standard configuration(add on the base)
Engine with fan | Intake and exhaust sysytem：Air filter and connecting pipes;Connecting flang of exhaust pipe
Alternator 65A 28V Starter motor 5kW 24V | Cooling system: Radiator;Connecting pipes;Fan guard;Belt guard
Note on A12: 作者: 不带风扇

## 4DF(E)
4DF Engine Technical Data
Engine model | 4110/125Z-09D | CA4DF2-12D
Type | 4-cylinder 4-stroke
Air intake type | Turbocharged | Turbocharged&intercooling
Cooling mode | Water cooling
Governor mode | electronic
Bore×Stroke(mm） | 110×125
Compression ratio | 17.5∶1
Rated speed(rpm) | 1500
Displacement(L) | 4.75
Rated power(without fan)(kW) | 65 | 84
Standby power(without fan)(kW) | 72 | 92
Fuel consumption(g/kWh) | 215 | 205
Oil consumption(L/h) | 0.08 | 0.08
Steady state speed regulation(%) | ≤3
Oil capacity including filter(L) | 16
Emission compliant | StageⅡ
The flywheel shell interface | SAE3
Flywheel for 11.5″flexible coupling
Dry weight of Gen Pac(kg) | 609 | 620
Overall dimension(mm) | 1353×680×952
Fan consumption（kW） | 4 | 4
27℃ air consumption（m3/min） | 4.6 | 5.3
Heat rejection of exhaust（kW） | 46 | 55
Exhaust gas temperature after turbine（℃） | 450 | 450
Exhaust gas flow（m3/min） | 12.3 | 14.2
Heat rejection from engine（kW） | 4.3 | 4.8
Heat rejection of coolant（kW） | 36 | 40
Base configuration | Standard configuration(add on the base)
Engine with fan | Intake and exhaust sysytem：Air filter and connecting pipes;Connecting flang of exhaust pipe
Alternator 65A 28V Starter motor 5kW 24V | Cooling system: Radiator;Connecting pipes;Fan guard;Belt guard
Note on A12: 作者: 不带风扇

## 4DX(E)
4DX Engine Technical Data
Engine model | 4DX21-45D | 4DX22-50D | 4DX23-65D
Type | 4-cylinder 4-stroke
Air intake type | Natural | Turbocharged | Turbo&intercooling
Cooling mode | Water cooling
Governor mode | Mechanical&electronic
Bore×Stroke(mm） | 102×118
Compression ratio | 17∶1
Rated speed(rpm) | 1500
Displacement(L) | 3.86
Rated power(without fan)(kW) | 33 | 37 | 48
Standby power(without fan)(kW) | 36 | 41 | 53
Fuel consumption(g/kWh) | 230 | 220 | 215
Oil consumption(L/h) | 0.06 | 0.05 | 0.05
Steady state speed regulation(%) | ≤5 | ≤5 | ≤5
Oil capacity including filter(L) | 12.5 | 13 | 13
Emission compliant | StageⅡ
The flywheel shell interface | SAE3
Flywheel for 11.5″flexible coupling
Dry weight of base(kg) | 350 | 380 | 380
Dry weight of Gen Pac(kg) | 375 | 405 | 410
Overall dimension(base)(mm) | 810×680×800 | 810×700×850
Overall dimension(G.P)(mm) | 1155×680×835 |  | 1480×705×900
Fan consumption（kW） | 2 | 2.5 | 3
27℃ air consumption（m3/min） | 2.6 | 3.2 | 3.9
Heat rejection of exhaust（kW） | 34.5 | 36.4 | 43.5
Exhaust gas temperature after turbine（℃） | 580 | 480 | 480
Exhaust gas flow（m3/min） | 8.3 | 8.4 | 10.4
Heat rejection from engine（kW） | 2 | 2.6 | 3.3
Heat rejection of coolant（kW） | 21.5 | 24.1 | 29
Base configuration | Standard configuration(add on the base)
Engine with fan | Intake and exhaust sysytem：Air filter and connecting pipes;Connecting flang of exhaust pipe
Alternator 35A 28V Starter motor 4.5kW 24V | Cooling system: Radiator with connecting pipes;Fan guard;Belt guard
Note on A12: 作者: 不带风扇

## 4DW (E)
4DW Engine Technical Data
Engine model | 4DW81-23D | 4DW91-29D | 4DW92-35D | 4DW93-42D
Type | 4-cylinder 4-stroke
Air intake type | Natural | Natural | Turbocharged | Turbo&intercool
Cooling mode | Water cooling
Governor mode | Mechanical&electronic
Bore×Stroke(mm） | 85×100 | 90×100
Compression ratio | 17∶1
Rated speed(rpm) | 1500
Displacement(L) | 2.27 | 2.54
Rated power(without fan)(kW) | 17 | 21 | 26 | 31
Standby power(without fan)(kW) | 19 | 23 | 29 | 34
Fuel consumption(g/kWh) | 240 | 240 | 230 | 216
Oil consumption(L/h) | 0.05 | 0.05 | 0.04 | 0.04
Steady state speed regulation(%) | ≤5 | ≤5 | ≤5 | ≤5
Oil capacity including filter(L) | 7.8 | 8 | 8 | 8
Emission compliant | StageⅡ
The flywheel shell interface | SAE4
Flywheel for 7.5″& 10″flexible coupling
Dry weight of base(kg) | 220 | 220 | 240 | 240
Dry weight of Gen Pac(kg) | 240 | 240 | 260 | 280
Overall dimension(base)(mm) | 750×555×680 | 750×555×680 | 750×600×735
Overall dimension(G.P)(mm) | 920×610×760 |  | 1120×810×760
Fan consumption（kW） | 1.2 | 1.6 | 1.8 | 2
27℃ air consumption（m3/min） | 1.4 | 1.7 | 2.1 | 2.4
Heat rejection of exhaust（kW） | 17.2 | 17.4 | 20.6 | 23.1
Exhaust gas temperature after turbine（℃） | 550 | 450 | 450 | 450
Exhaust gas flow（m3/min） | 4.2 | 4.6 | 5.9 | 6.7
Heat rejection from engine（kW） | 1.1 | 1.3 | 1.6 | 1.9
Heat rejection of coolant（kW） | 11 | 13.7 | 16.9 | 17.1
Base configuration | Standard configuration(add on the base)
Engine with fan | Intake and exhaust sysytem：Air filter and connecting pipes;Connecting flang of exhaust pipe
Alternator 500W 14V Starter motor 3.5kW 12V | Cooling system: Radiator with connecting pipes;Fan guard;Belt guard
Note on A12: 作者: 不带风扇

## 1500E
Collection of FAWDE gen-set diesel engine
Rated speed：1500rpm
Engine type | Standby power（kWm） | Prime power（kW） | Gen-set power（kWe） | Fan consumption（kW） | Intake type | Displacement（L） | Governor mode | Emission
4DW81-23D | 19 | 17 | 12 | 1.2 | natural | 2.26 | Mechanical/Electronic | stageⅡ
4DW91-29D | 23 | 21 | 16 | 1.6 | natural | 2.54 | Mechanical/Electronic | stageⅡ
4DW92-35D | 29 | 26 | 20 | 1.8 | turbo | 2.54 | Mechanical/Electronic | stageⅡ
4DW93-42D | 34 | 31 | 24 | 2 | turbo&intercooling | 2.54 | Mechanical/Electronic | stageⅡ
4DX21-45D | 36 | 33 | 24 | 2.5 | natural | 3.86 | Mechanical/Electronic | stageⅡ
4DX22-50D | 41 | 37 | 30 | 2.5 | turbo | 3.86 | Mechanical/Electronic | stageⅡ
4DX23-65D | 53 | 48 | 38 | 3 | turbo&intercooling | 3.86 | Mechanical/Electronic | stageⅡ
4110/125Z-09D | 72 | 65 | 54 | 4 | turbo | 4.75 | Electronic | stageⅡ
CA4DF2-12D | 92 | 84 | 72 | 4 | turbo&intercooling | 4.75 | Electronic | stageⅡ
CA6DF2D-14D | 105 | 96 | 80 | 8 | turbo | 6.55 | Electronic | stageⅡ
CA6DF2-17D | 138 | 125 | 100 | 8 | turbo | 7.13 | Electronic | stageⅡ
CA6DF2-19D | 154 | 140 | 120 | 8 | turbo&intercooling | 7.13 | Electronic | stageⅡ
CA6DL1-24D | 194 | 176 | 150 | 8 | turbo&intercooling | 7.7 | Electronic | stageⅡ
CA6DL2-27D | 226 | 205 | 180 | 9 | turbo&intercooling | 8.57 | Electronic | stageⅡ
CA6DL2-30 | 251 | 227 | 200 | 9 | turbo&intercooling | 8.57 | Electronic | stageⅡ
CA6DM2-39D | 316 | 287 | 250 | 11 | turbo&intercooling | 11.04 | ECU | EuroⅢ
CA6DM2J-39D | 316 | 287 | 250 | 11 | turbo&intercooling | 11.04 | Electronic | stageⅡ
CA6DM2-41D | 330 | 300 | 270 | 11 | turbo&intercooling | 11.04 | ECU | EuroⅢ
CA6DM2J-41D | 330 | 300 | 270 | 11 | turbo&intercooling | 11.04 | Electronic | stageⅡ
CA6DN1-45D | 365 | 332 | 300 | 11 | turbo&intercooling | 12.53 | ECU | EuroⅢ
CA6DN1J-45D | 365 | 332 | 300 | 11 | turbo&intercooling | 12.53 | Electronic | stageⅡ